## Version
Clean Power VFD BACnet specifications (Beta)
The Clean Power VFD supports BACnet IP over UDP protocol, UDP port: 47808 by default.
Version | Date | Author | Author 2 | Description
1.0 | 2024-02-26 | jmlegrand@smartd.co | jml | Inital draft WIP
1.1 | 2024-07-24 | bton@smartd.co | pb | Alarms starts from BV500
1.2 | 2024-09-09 |  | pb | Change alarm acknowledgement: 0: To acknowledge, 1: No action Change reset lockout to read/command: in Read: 0: No lockout, 1: Lockout in Command: 0: Reset lockout, 1: No action Change remoteControlMode and remoteControlSource to read/command
1.3 | 2024-11-19 |  | pb | Add Motor Controller State "Magnetizing" Fix documentation for motor controller state (Paused = 6 and Autotuning = 7)
1.4 | 2025-02-05 |  | pb | Added PID multistate variable MV455
1.5 | 2025-06-16 |  | dob | Added Motor Controller State "Starting" Added new alarm codes (ALARM_CODE_PIN_INVALID to ALARM_CODE_EMERGENCY_MODE_FORBIDDEN)
1.5 | 2025.06.18 |  | pb | Added MSV_SYSTEM_RUN_MODE_MAINTENANCE
1.6 | 2025.07.22 |  | pb | Added Analog and Binary input (AI, BI)
1.7 | 2025.07.25 |  | pb | Fixed Maintenance mode MSV values to match implementation
1.8 | 2025.10.09 |  | mp | Updated device info documentation to use the standard protocol values
1.9 | 2025.12.04 |  | mbf | Labelled unimpleted objects and implemented objects Added External alarms BV574 to 577 + Acknowledge BV774 to 777
1.10 | 2025.12.09 |  | dob | Added 'motor thermal overload' alarm
1.11 | 2026.01.08 |  | mbf | Removed hidden tabs
1.12 | 2026.01.28 |  | pb | Device info "Firmware Revision" updated to match implementation
1.13 | 2026.02.09 |  | af | Updated status of configuration (AV200 to 205) and metrics (AV900 to 906) to implemented
1.14 | 2026.02.11 |  | fw | Added internal mcu comm loss alarm
1.15 | 2026.03.25 |  | pb | Added System.Heartbeat and BACNET_COMM_LOSS alarm
1.16 | 2026.06.20 |  | pb | Added analaog output status objects AO1 and AO2

## BACnet Object List
SmartD BACnet Object ID Definition Guideline |  |  | Status
BI | 0..6 | IOs Physical digital inputs | Implemented
BO | 0..2 | IOs Physical digital outputs / relays | Not implemented
AI | 0..2 | IOs Physical analog inputs | Implemented
AO | 0..1 | IOs Physical analog outputs | Not implemented
BV, AV, MV | 0..29 | Motor Controller | Implemented
BV, AV, MV | 30..99 | System | Implemented
BV, AV, MV | 100..199 | Power Meter | Implemented
BV, AV, MV | 200..399 | Configuration | Not implemented
BV, AV, MV | 400..449 | Cooling Management | Not implemented
BV, AV, MV | 450..499 | PID | Implemented
BV, AV, MV | 500-699 | Alarm active state | Implemented
BV, AV, MV | 700-899 | Alarm acknowledge | Implemented
BV, AV, MV | 900-1099 | Metrics | Not implemented

## Device Info
The Clean Power VFD MUST support as BACnet Application Specific Controller (B-ASC) profile.
It MUST support the BACnet Device object with the following object properties:
Device object property | Value | Access type | Notes | Status
Object Identifier |  | Writable | User-defined Identifier (32-bit integer: 0-4294967295 ). Default: . Example: | Implemented
Object Name | Clean Power VFD {serial number} | Writable | User-defined name (Maximum length: 255 characters). Default: Clean Power VFD {serial number} Valid characters: 0-9, a-z, A-Z, Space, -, _ Example: Clean Power VFD 000020220505000201 | Implemented
Object Type | 8 | Read-only | DEVICE | Implemented
Description | Clean Power VFD {Input voltage} {kW}kW {HP}HP | Writable | User-defined description (Maximum length: 255 characters) Default: Clean Power VFD {Input voltage} {kW}kW {HP}HP. Valid characters: 0-9, a-z, A-Z, Space, -, _ Example: Clean Power VFD 480V 18.5kW 25HP | Implemented
System Status | {Current VFD system status} | Read-only | 0: Operational 1: Operational read-only 2: Download required 3: Download in progress 4: Non operational 5: Backup in progress | Implemented
Location (Optional) |  | Writable | User-define location (Maximum length: 50 characters). Default: Blank Valid characters: 0-9, a-z, A-Z, Space, -, _ Example: Mechanical room #1 | Implemented
Vendor Name | SmartD Technologies | Read-only |  | Implemented
Vendor Identifier | SmartD BACnet identifier (to check) | Read-only |  | Implemented
Model Name | {Clean Power VFD part number} | Read-only | Example: SDB-1-2185-A for 480V 3PH 18.5kW-25HP | Implemented
Firmware Revision | {Active bacnet stack version} | Read-only | 1.3.6 | Implemented
Application Software Revision | {Active software version} | Read-only | Example: 2023.09.00-40 | Implemented
Protocol Version | 1 | Read-only | BACnet protocol version | Implemented
Protocol Revision | 14 | Read-only | BACnet protocol revision (at least 14) | Implemented
Services Supported | ReadProperty, WriteProperty, | Read-only |  | Implemented
Object Types Supported | Binary Input, Binary Output, Binary Value, Analog Input, Analog Output, Analog Value, Multi-state Value | Read-only |  | Implemented
Object Lists | List of all BACnet objects defined in the Clean Power VFD | Read-only |  | Implemented
Max APDU Length Accepted | 480 | Read-only |  | Implemented
Segmentation Supported | 3 | Read-only | 3: No segmentation | Implemented
APDU Timeout | 3000 | Writable | User-defined timeout in milliseconds between 1000-65535. Default: 3000ms | Implemented
Number of APDU Retries | 3 | Writable | User-defined number of retries between 2 and 10. Default: 3 | Implemented
Max Master | 127 | Writable | 127. Not writable via BACnet services | Implemented
Max Info Frames | 1 | Writable | Not writable | Implemented
Device Address Binding | None | Read-only | No supported | Implemented
Database Revision (Optional) |  | Read-only |  | Implemented

## Analog Outputs
BACnet Object Type | BACnet Object | BACnet Object Name | Access Type | Range | Status
Analog Output | AO0 | IOs.OperationalData.analogOutput1 | Read/Command | 0 .. 100% | Implemented
| AO1 | IOs.OperationalData.analogOutput2 | Read/Command | 0 .. 100% | Implemented

## Digital Inputs
BACnet Object Type | BACnet Object | BACnet Object Name | Access Type | Range | Status
Binary Input | BI1 | IOs.OperationalData.digitalInput1 | Read | 0: Output is low, not configured, or configured as encoder, 1: Output is high | Implemented
| BI2 | IOs.OperationalData.digitalInput2 | Read | 0: Output is low, not configured, or configured as encoder, 1: Output is high | Implemented
| BI3 | IOs.OperationalData.digitalInput3 | Read | 0: Output is low, not configured, or configured as encoder, 1: Output is high | Implemented
| BI4 | IOs.OperationalData.digitalInput4 | Read | 0: Output is low, not configured, or configured as encoder, 1: Output is high | Implemented
| BI5 | IOs.OperationalData.digitalInput5 | Read | 0: Output is low, not configured, or configured as encoder, 1: Output is high | Implemented
| BI6 | IOs.OperationalData.digitalInput6 | Read | 0: Output is low, not configured, or configured as encoder, 1: Output is high | Implemented

## Relays
BACnet Object Type | BACnet Object | BACnet Object Name | Access Type | Range | Status
Binary Output | BO0 | IOs.OperationalData.relay1 | Read/Command | 0: Off 1: On | Implemented
| BO1 | IOs.OperationalData.relay2 | Read/Command | 0: Off 1: On | Implemented
| BO2 | IOs.OperationalData.relay3 | Read/Command | 0: Off 1: On | Implemented

## Analog Inputs
BACnet Object Type | BACnet Object | BACnet Object Name | Access Type | Range | Status
Analog Input | AI1 | IOs.OperationalData.analogInput1 | Read | 0 .. 100% | Implemented
| AI2 | IOs.OperationalData.analogInput2 | Read | 0 .. 100% | Implemented
| AI3 | IOs.OperationalData.analogInput3 | Read | 0 .. 100% | Implemented

## Motor Controller
BACnet Object Type | BACnet Object | BACnet Object Name | Access Type | Range | Status | Notes
Multi-State Value | MV0 | Motor Controller.OperationalData.motor_state | Read | 1: Disabled 2: Halted 3: Ramping up 4: Running 5: Ramping down 6: Paused 7: Autotuning 8: Magnetizing 9: Starting | Implemented | Object Implemented, 'Starting' state is not implemented yet
Multi-State Value | MV1 | Motor Controller.OperationalData.direction | Read | 1: Forward 2: Reverse | Implemented
Multi-State Value | MV2 | Motor Controller.OperationalData.mode | Read | 1: Frequency mode 2: Preset frequency mode 3: Velocity mode 4: Preset velocity mode | Implemented
Analog Value | AV3 | Motor Controller.OperationalData.frequency | Read | 0..120 Hz | Implemented
Analog Value | AV4 | Motor Controller.OperationalData.velocity | Read | 0..7200 RPM | Implemented
Analog Value | AV5 | Motor Controller.OperationalData.torque | Read | -250..+250 % | Implemented
Multi-State Value | MV10 | Motor Controller.SetPoints.command | Command | 1: ON 2: OFF | Implemented
Multi-State Value | MV11 | Motor Controller.SetPoints.direction | Command | 1: Forward 2: Reverse | Implemented
Analog Value | AV12 | Motor Controller.SetPoints.frequency | Command | 0..120 Hz | Implemented
Analog Value | AV13 | Motor Controller.SetPoints.velocity | Command | 0..7200 RPM | Implemented
Analog Value | AV14 | Motor Controller.SetPoints.torque | Command | -250..+250 % | Implemented
Multi-State Value | MV15 | Motor Controller.SetPoints.mode | Command | 1: Frequency mode 2: Preset frequency mode 3: Velocity mode 4: Preset velocity mode 5: Torque mode 6: Preset torque mode | Implemented
Multi-State Value | MV16 | Motor Controller.SetPoints.presetFrequency | Command | 1: Preset frequency 1 2: Preset frequency 2 3: Preset frequency 3 4: Preset frequency 4 5: Preset frequency 5 6: Preset frequency 6 7: Preset frequency 7 8: Preset frequency 8 | Implemented
Multi-State Value | MV17 | Motor Controller.SetPoints.presetVelocity | Command | 1: Preset velocity 1 2: Preset velocity 2 3: Preset velocity 3 4: Preset velocity 4 5: Preset velocity 5 6: Preset velocity 6 7: Preset velocity 7 8: Preset velocity 8 | Implemented
Multi-State Value | MV18 | Motor Controller.SetPoints.presetTorque | Command | 1: Preset torque 1 2: Preset torque 2 3: Preset torque 3 4: Preset torque 4 5: Preset torque 5 6: Preset torque 6 7: Preset torque 7 8: Preset torque 8 | Implemented
Analog Value | AV19 | Motor Controller.SetPoints.minTorque | Command | -500..+500 % | Not implemented
Analog Value | AV20 | Motor Controller.SetPoints.maxTorque | Command | -500..+500 % | Not implemented
Multi-State Value | MV21 | Motor Controller.SetPoints.rampUpCurve | Command | 1: Curve 1 2: Curve 2 3: Curve 3 4: Curve 4 | Implemented
Multi-State Value | MV22 | Motor Controller.SetPoints.rampDownCurve | Command | 1: Curve 1 2: Curve 2 3: Curve 3 4: Curve 4 | Implemented

## System
BACnet Object Type | BACnet Object | BACnet Object Name | Access Type | Range | Status
Binary Value | BV30 | System.ResetLockout | Read/Command | Read: 0: No lockout, 1: Lockout Command: 0: Reset lockout, 1: No action | Implemented
Multi-State Value | MV31 | System.OperationalData.system_state | Read | 1: Booting 2: Unconfigured (no configuration) 3: Ready To Run 4: Running Auto-tuning 5: Running Normal 6: Running in Emergency Mode 7: Running in Out Of Service 8: Lockout 9: Shutting down 10: Factory Reset 11: Fault 12: Need auto-tuning 13: Running degraded 14: Hardware test 15: Software version change | Implemented
Multi-State Value | MV40 | System.Setpoints.remoteControlMode | Read/Command | 1: Local 2: Remote | Implemented
Multi-State Value | MV41 | System.Setpoints.remoteControlSource | Read/Command | 1: Remote source 1 2: Remote source 2 | Implemented
Multi-State Value | MSV42 | System.Setpoints.MaintenanceMode | Read/Command | 1: active 2: inactive | Implemented
Analog Value | AV43 | System.Heartbeat | Read/Command | Read: Counter that increment every second Write:Kick BACNET AlarmCommLoss watchdog | Implemented

## Power Meter
BACnet Object Type | BACnet Object | BACnet Object Name | Access Type | Range | Multiplier | Status
Analog Value | AV100 | Power Meter.OperationalData.line.L1_current | Read | 0..(depending of the model, max 165A) A | 1 | Implemented
| AV101 | Power Meter.OperationalData.line.L2_current | Read | 0..(depending of the model, max 165A) A | 1 | Implemented
| AV102 | Power Meter.OperationalData.line.L3_current | Read | 0..(depending of the model, max 165A) A | 1 | Implemented
| AV103 | Power Meter.OperationalData.line.L12_voltage | Read | 0..(depending of the model, max: 600V) V | 1 | Implemented
| AV104 | Power Meter.OperationalData.line.L23_voltage | Read | 0..(depending of the model, max: 600V) V | 1 | Implemented
| AV105 | Power Meter.OperationalData.line.L31_voltage | Read | 0..(depending of the model, max: 600V) V | 1 | Implemented
| AV106 | Power Meter.OperationalData.line.frequency | Read | 0..100 Hz | 1 | Implemented
| AV107 | Power Meter.OperationalData.line.real_power | Read | 0..(depending of the model, max: 120000) W | 0.01 | Implemented
| AV108 | Power Meter.OperationalData.line.apparent_power | Read | 0..(depending of the model, max: 120000) VA | 0.01 | Implemented
| AV109 | Power Meter.OperationalData.line.reactive_power | Read | -100000..+100000 VAR | 0.01 | Implemented
| AV110 | Power Meter.OperationalData.line.power_factor | Read | -1.00 ... 1.00 | 100 | Implemented
Implemented
| AV140 | Power Meter.OperationalData.motor.U_current | Read | 0..(depending of the model, max 165A) A | 1 | Implemented
| AV141 | Power Meter.OperationalData.motor.V_current | Read | 0..(depending of the model, max 165A) A | 1 | Implemented
| AV142 | Power Meter.OperationalData.motor.W_current | Read | 0..(depending of the model, max 165A) A | 1 | Implemented
| AV143 | Power Meter.OperationalData.motor.UV_voltage | Read | 0..(depending of the model, max: 600V) V | 1 | Implemented
| AV144 | Power Meter.OperationalData.motor.VW_voltage | Read | 0..(depending of the model, max: 600V) V | 1 | Implemented
| AV145 | Power Meter.OperationalData.motor.WU_voltage | Read | 0..(depending of the model, max: 600V) V | 1 | Implemented
| AV146 | Power Meter.OperationalData.motor.frequency | Read | 0..100 Hz | 1 | Implemented
| AV147 | Power Meter.OperationalData.motor.balance | Read | 0..100 % | 1 | Implemented
| AV148 | Power Meter.OperationalData.motor.real_power | Read | 0..(depending of the model, max: 120000) W | 0.01 | Implemented
| AV149 | Power Meter.OperationalData.motor.apparent_power | Read | 0..(depending of the model, max: 120000) VA | 0.01 | Implemented
| AV150 | Power Meter.OperationalData.motor.reactive_power | Read | -100000..+100000 VAR | 0.01 | Implemented
| AV151 | Power Meter.OperationalData.motor.power_factor | Read | -1.00 ... 1.00 | 100 | Implemented
Implemented
| AV180 | Power Meter.OperationalData.dcbus.Vdc_plus_voltage | Read | 0..1000 V | 1 | Implemented
| AV181 | Power Meter.OperationalData.dcbus.Vdc_minus_voltage | Read | 0..1000 V | 1 | Implemented

## Configuration
BACnet Object Type | BACnet Object | BACnet Object Name | Access Type | Range | Status
Analog Value | AV200 | Motor Controller.Configuration.motorNameplate.nominalInputFrequency | Read | 50 or 60 Hz | Implemented
| AV201 | Motor Controller.Configuration.motorNameplate.nominalVelocity | Read | 0..7200 RPM | Implemented
| AV202 | Motor Controller.Configuration.motorNameplate.nominalVoltage | Read | 0..(480 or 600) V (depending on model) | Implemented
| AV203 | Motor Controller.Configuration.motorNameplate.nominalCurrent | Read | 0..(depending on model) A | Implemented
| AV204 | Motor Controller.Configuration.motorNameplate.minInputFrequency | Read | 0..119 Hz | Implemented
| AV205 | Motor Controller.Configuration.motorNameplate.maxInputFrequency | Read | 1..120 Hz | Implemented

## Cooling
BACnet Object Type | BACnet Object | BACnet Object Name | Access Type | Range | Status
Analog Value | AV400 | Cooling Management.OperationalData.driveTemperature | Read | -20.0..+140.0 °C | Not implemented
| AV401 | Cooling Management.OperationalData.driveAmbiantTemperature | Read | -20.0..+140.0 °C | Not implemented
| AV402 | Cooling Management.OperationalData.fanCount | Read | 1..4 | Not implemented
| AV403 | Cooling Management.OperationalData.fans[0].speed | Read | 0..65535 RPM | Not implemented
| AV404 | Cooling Management.OperationalData.fans[1].speed | Read | 0..65535 RPM | Not implemented
| AV405 | Cooling Management.OperationalData.fans[2].speed | Read | 0..65535 RPM | Not implemented
| AV406 | Cooling Management.OperationalData.fans[3].speed | Read | 0..65535 RPM | Not implemented

## PID
BACnet Object Type | BACnet Object | BACnet Object Name | Access Type | Range | Status
Multi-State Value | MV450 | PID1.Setpoints.outputMode | Read/Command | 1: Control mode (Closed loop) 2: Forced output mode | Implemented
Analog Value | AV451 | PID1.SetPoints.desiredProcessValue | Read/Command | depends on configuration | Implemented
| AV452 | PID1.SetPoints.forcedOutputValueFrequency | Read/Command | 0..7200 RPM | Implemented
| AV453 | PID1.SetPoints.forcedOutputValueVelocity | Read/Command | 0..60 Hz | Implemented
| AV454 | PID1.OperationalData.feedbackValue | Read | depends on configuration | Implemented
Multi-State Value | MV455 | PID1.OperationalData.state | Read | 0: UNSPECIFIED 1: DISABLED 2: OFF 3: DIRECT_ON 4: REVERSE_ON 5: SLEEP 6: GOING_TO_SLEEP 7: WAKING_UP 8: FORCED_OUTPUT 9: MOTOR_DISABLED 10: DEADBAND 11: CONSTANT_OUTPUT 12: STOPPING | Implemented

## Alarms
BACnet Object Type | BACnet Object | BACnet Object Name | Access Type | Range | Status | BACnet Object Type | BACnet Object | BACnet Object Name | Access Type | Range | Status
Binary Value | BV500 | Alarms.Unspecified | Read | 0: Inactive, 1: Active | Not implemented | Binary Value | BV700 | Alarms.Unspecified acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Not implemented | This alarm does not exist and is never raised, the related BV are never created and not exposed by server
| BV501 | Alarms.STO | Read | 0: Inactive, 1: Active | Implemented |  | BV701 | Alarms.STO acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV502 | Alarms.STO Loss | Read | 0: Inactive, 1: Active | Implemented |  | BV702 | Alarms.STO Loss acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV503 | Alarms.Line phase inversion | Read | 0: Inactive, 1: Active | Implemented |  | BV703 | Alarms.Line phase inversion acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV504 | Alarms.DC undervoltage | Read | 0: Inactive, 1: Active | Implemented |  | BV704 | Alarms.DC undervoltage acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV505 | Alarms.DC overvoltage | Read | 0: Inactive, 1: Active | Implemented |  | BV705 | Alarms.DC overvoltage acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV506 | Alarms.Line voltage sag | Read | 0: Inactive, 1: Active | Implemented |  | BV706 | Alarms.Line voltage sag acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV507 | Alarms.Line voltage balance | Read | 0: Inactive, 1: Active | Implemented |  | BV707 | Alarms.Line voltage balance acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV508 | Alarms.Line phase loss | Read | 0: Inactive, 1: Active | Implemented |  | BV708 | Alarms.Line phase loss acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV509 | Alarms.HMI communication loss | Read | 0: Inactive, 1: Active | Implemented |  | BV709 | Alarms.HMI communication loss acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV510 | Alarms.Line current balance | Read | 0: Inactive, 1: Active | Implemented |  | BV710 | Alarms.Line current balance acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV511 | Alarms.Line overcurrent | Read | 0: Inactive, 1: Active | Implemented |  | BV711 | Alarms.Line overcurrent acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV512 | Alarms.Motor current balance | Read | 0: Inactive, 1: Active | Implemented |  | BV712 | Alarms.Motor current balance acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV513 | Alarms.Motor overcurrent | Read | 0: Inactive, 1: Active | Implemented |  | BV713 | Alarms.Motor overcurrent acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV514 | Alarms.Motor overtemp | Read | 0: Inactive, 1: Active | Implemented |  | BV714 | Alarms.Motor overtemp acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV515 | Alarms.Motor Overload | Read | 0: Inactive, 1: Active | Implemented |  | BV715 | Alarms.Motor overload acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV516 | Alarms.Drive overtemp | Read | 0: Inactive, 1: Active | Implemented |  | BV716 | Alarms.Drive overtemp acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV517 | Alarms.Unknown boot state | Read | 0: Inactive, 1: Active | Implemented |  | BV717 | Alarms.Unknown boot state acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV518 | Alarms.Booted backup software | Read | 0: Inactive, 1: Active | Implemented |  | BV718 | Alarms.Booted backup software acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV519 | Alarms.Booted backup software with default config | Read | 0: Inactive, 1: Active | Implemented |  | BV719 | Alarms.Booted backup software with default config acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV520 | Alarms.Drive high temperature | Read | 0: Inactive, 1: Active | Implemented |  | BV720 | Alarms.Drive high temperature acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV521 | Alarms.Line voltage swell | Read | 0: Inactive, 1: Active | Implemented |  | BV721 | Alarms.Line voltage swell acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV522 | Alarms.Software update failed | Read | 0: Inactive, 1: Active | Implemented |  | BV722 | Alarms.Software update failed acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV523 | Alarms.DC single phased | Read | 0: Inactive, 1: Active | Implemented |  | BV723 | Alarms.DC single phased acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV524 | Alarms.Cooling fan 1 fault | Read | 0: Inactive, 1: Active | Implemented |  | BV724 | Alarms.Cooling fan 1 fault acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV525 | Alarms.Cooling fan 2 fault | Read | 0: Inactive, 1: Active | Implemented |  | BV725 | Alarms.Cooling fan 2 fault acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV526 | Alarms.Cooling fan 3 fault | Read | 0: Inactive, 1: Active | Implemented |  | BV726 | Alarms.Cooling fan 3 fault acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV527 | Alarms.Cooling fan 4 fault | Read | 0: Inactive, 1: Active | Implemented |  | BV727 | Alarms.Cooling fan 4 fault acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV528 | Alarms.Cooling fan capacity fault | Read | 0: Inactive, 1: Active | Implemented |  | BV728 | Alarms.Cooling Fan Capacity Fault acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV529 | Alarms.Line unexpected voltage | Read | 0: Inactive, 1: Active | Implemented |  | BV729 | Alarms.Line unexpected voltage acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV530 | Alarms.Low level comm errors | Read | 0: Inactive, 1: Active | Implemented |  | BV730 | Alarms.Low level comm errors acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV531 | Alarms.DC unbalanced | Read | 0: Inactive, 1: Active | Implemented |  | BV731 | Alarms.DC unbalanced acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV532 | Alarms.Drive output overcurrent | Read | 0: Inactive, 1: Active | Implemented |  | BV732 | Alarms.Drive output overcurrent acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV533 | Alarms.Simultaneous forward and reverse command | Read | 0: Inactive, 1: Active | Implemented |  | BV733 | Alarms.Simultaneous forward and reverse command acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV534 | Alarms.System boot time exceeded | Read | 0: Inactive, 1: Active | Implemented |  | BV734 | Alarms.System boot time exceeded acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV535 | Alarms.System degraded | Read | 0: Inactive, 1: Active | Implemented |  | BV735 | Alarms.System degraded acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV536 | Alarms.Abnormal CPU usage | Read | 0: Inactive, 1: Active | Implemented |  | BV736 | Alarms.Abnormal CPU usage acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV537 | Alarms.Abnormal memory usage | Read | 0: Inactive, 1: Active | Implemented |  | BV737 | Alarms.Abnormal memory usage acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV538 | Alarms.DC overvoltage stall prevention | Read | 0: Inactive, 1: Active | Implemented |  | BV738 | Alarms.DC overvoltage stall prevention acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV539 | Alarms.Motor overcurrent stall prevention | Read | 0: Inactive, 1: Active | Implemented |  | BV739 | Alarms.Motor overcurrent stall prevention acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV540 | Alarms.Line unexpected frequency | Read | 0: Inactive, 1: Active | Implemented |  | BV740 | Alarms.Line unexpected frequency acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV541 | Alarms.DC unexpected voltage | Read | 0: Inactive, 1: Active | Implemented |  | BV741 | Alarms.DC unexpected voltage acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV542 | Alarms.AFE fault | Read | 0: Inactive, 1: Active | Implemented |  | BV742 | Alarms.AFE fault acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV543 | Alarms.AFE low voltage ride through | Read | 0: Inactive, 1: Active | Implemented |  | BV743 | Alarms.AFE low voltage ride through acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV544 | Alarms.Remote to local override | Read | 0: Inactive, 1: Active | Implemented |  | BV744 | Alarms.Remote to local override acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV545 | Alarms.Analog output sensor loss | Read | 0: Inactive, 1: Active | Implemented |  | BV745 | Alarms.Analog output sensor loss acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV546 | Alarms.PID 1 low process value | Read | 0: Inactive, 1: Active | Implemented |  | BV746 | Alarms.PID 1 low process value acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV547 | Alarms.PID 1 high process value | Read | 0: Inactive, 1: Active | Implemented |  | BV747 | Alarms.PID 1 high process value acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV548 | Alarms.Control board power loss | Read | 0: Inactive, 1: Active | Implemented |  | BV748 | Alarms.Control board power loss acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV549 | Alarms.Motor control instability | Read | 0: Inactive, 1: Active | Implemented |  | BV749 | Alarms.Motor control instability acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV550 | Alarms.Motor overspeed | Read | 0: Inactive, 1: Active | Implemented |  | BV750 | Alarms.Motor overspeed acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV551 | Alarms.Motor underspeed | Read | 0: Inactive, 1: Active | Implemented |  | BV751 | Alarms.Motor underspeed acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV552 | Alarms.Motor wrong direction | Read | 0: Inactive, 1: Active | Implemented |  | BV752 | Alarms.Motor wrong direction acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV553 | Alarms.Encoder speed error | Read | 0: Inactive, 1: Active | Implemented |  | BV753 | Alarms.Encoder speed error acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV554 | Alarms.Encoder communication failure | Read | 0: Inactive, 1: Active | Implemented |  | BV754 | Alarms.Encoder communication failure | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV555 | Alarms.Analog input 1 sensor loss | Read | 0: Inactive, 1: Active | Implemented |  | BV755 | Alarms.Analog input 1 sensor loss acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV556 | Alarms.Analog input 2 sensor loss | Read | 0: Inactive, 1: Active | Implemented |  | BV756 | Alarms.Analog input 2 sensor loss acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV557 | Alarms.Analog input 3 sensor loss | Read | 0: Inactive, 1: Active | Implemented |  | BV757 | Alarms.Analog input 3 sensor loss acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV558 | Alarms.Modbus communication loss | Read | 0: Inactive, 1: Active | Implemented |  | BV758 | Alarms.Modbus communication loss acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV569 | Alarms.High ambient temperature | Read | 0: Inactive, 1: Active | Implemented |  | BV769 | Alarms.High ambient temperature acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV560 | Alarms.Motor temperature sensor shorted | Read | 0: Inactive, 1: Active | Implemented |  | BV760 | Alarms.Motor temperature sensor shorted acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV561 | Alarms.Motor phase loss | Read | 0: Inactive, 1: Active | Implemented |  | BV761 | Alarms.Motor phase loss acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV562 | Alarms.Motor stalled | Read | 0: Inactive, 1: Active | Implemented |  | BV762 | Alarms.Motor stalled acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV563 | Alarms.Motor disconnected | Read | 0: Inactive, 1: Active | Implemented |  | BV763 | Alarms.Motor disconnected acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV564 | Alarms.Application underload | Read | 0: Inactive, 1: Active | Implemented |  | BV764 | Alarms.Application underload acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV565 | Alarms.Motor autorestart failure | Read | 0: Inactive, 1: Active | Implemented |  | BV765 | Alarms.Motor autorestart failure acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV566 | Alarms.AFE low voltage ride through cannot recover | Read | 0: Inactive, 1: Active | Implemented |  | B5766 | Alarms.AFE low voltage ride through cannot recover acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV567 | Alarms.Drive overload | Read | 0: Inactive, 1: Active | Implemented |  | BV767 | Alarms.Drive overload acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV568 | Alarms.Pin invalid | Read | 0: Inactive, 1: Active | Implemented |  | BV768 | Alarms.Pin invalid acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV569 | Alarms.Damper feedback loss | Read | 0: Inactive, 1: Active | Implemented |  | BV769 | Alarms.Damper feedback loss acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV570 | Alarms.External start feedback timeout | Read | 0: Inactive, 1: Active | Implemented |  | BV770 | Alarms.External start feedback timeout acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV571 | Alarms.External post stop feedback timeout | Read | 0: Inactive, 1: Active | Implemented |  | BV771 | Alarms.External post stop feedback timeout acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV572 | Alarms.Motor ground fault | Read | 0: Inactive, 1: Active | Implemented |  | BV772 | Alarms.Motor ground fault acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV573 | Alarms.Emergency mode forbidden | Read | 0: Inactive, 1: Active | Implemented |  | BV773 | Alarms.Emergency mode forbidden acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV574 | Alarms.External 1 | Read | 0: Inactive, 1: Active | Implemented |  | BV774 | Alarms.External 1 acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV575 | Alarms.External 2 | Read | 0: Inactive, 1: Active | Implemented |  | BV775 | Alarms.External 2 acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV576 | Alarms.External 3 | Read | 0: Inactive, 1: Active | Implemented |  | BV776 | Alarms.External 3 acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV577 | Alarms.External 4 | Read | 0: Inactive, 1: Active | Implemented |  | BV777 | Alarms.External 4 acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV578 | Alarms.Motor thermal overload | Read | 0: Inactive, 1: Active | Implemented |  | BV778 | Alarms.Motor thermal overload acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV579 | Alarms.Internal MCU communication loss | Read | 0: Inactive, 1: Active | Implemented |  | BV779 | Alarms.Motor thermal overload acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented
| BV580 | Alarms.Bacnet communication loss | Read | 0: Inactive, 1: Active | Implemented |  | BV780 | Alarms.Bacnet communication loss acknowledge | Read/Command | 0: Acknowledge alarm, 1: No action | Implemented

## Metrics
BACnet Object Type | BACnet Object | BACnet Object Name | Access Type | Range | Multiplier | Status
Analog Value | AV900 | Motor Controller.Metrics.lifeTime.startCount | Read | 0..4294967296 |  | Implemented
| AV901 | Motor Controller.Metrics.lifeTime.runTime | Read | 0..4294967296 (hours) |  | Implemented
| AV902 | Motor Controller.Metrics.runTime.startCount | Read | 0..4294967296 |  | Implemented
| AV903 | Motor Controller.Metrics.runTime.runTime | Read | 0..4294967296 (hours) |  | Implemented
| AV904 | Motor Controller.Metrics.MotorLifeTime.startCount | Read | 0..4294967296 |  | Implemented
| AV905 | Motor Controller.Metrics.MotorLifeTime.runTime | Read | 0..4294967296 (hours) |  | Implemented
| AV906 | Motor Controller.Metrics.MotorRunTime.runTime | Read | 0..4294967296 (hours) |  | Implemented