## Version
| Date | Author | Description
2.0 | 2023-06-01 | jml | Inital draft of version v2 * Added version and profile registers * Updated links to update automatically
2.1 | 2023-09-12 | jml | * Added registers to expose temperatures and fans count (not implemented yet) * Added documentation of Device Info code 43 request/responses (not implemented yet)
2.2 | 2023-09-26 | jml | * Added registers for torque (not implemented yet) * Added motor nameplate (not implemented yet) * Added I/Os state registers (not implemented yet) * Added motor controller metrics (not implemented yet)
2.3 | 2023-12-12 | dm | * Added PID
2.4 | 2024-02-22 | pb | * Added analog input sensor loss alarms
2.5 | 2024-03-14 | dm | * Added modbus communication loss alarm
2.6 | 2024-03-19 | jml | * Modified Device Info to specifc Slave Number 0x01. The MODBUS/TCP server only accept requests with slave number sets to 0x01
2.7 | 2024-04-11 | cd | * Added High Ambient Temperature alarm * Added MotorTemperature Sensor Loss alarm
2.8 | 2024-05-03 | pb | * Added motor controller Metrics * Added cooling Metrics & OpData
2.9 | 2024-05-13 | pb | * Added motor Torque OpData
2.10 | 2024-05-27 | dm | * Added new state (system version change)
2.11 | 2024-05-29 | pb | * Added System Metrics
2.12 | 2024-05-30 | af | * Added torque in operational data * Added torque, presetTorque, minTorqueLimit and maxTorqueLimit in setpoints * Added Torque Mode and Preset Torque Mode to MCM enum * Added PID forced torque output * Fixed AL4/AL5 registers for new alarms (motor phase loss, motor stalled, motor disconnected, motor application underlay and motor auto-restart failure)
2.13 | 2024-07-16 | dob | * Mark torque control setpoint registers as not implemented * Review for release of v2024.09.00
2.14 | 2024-07-25 | af | * Torque setpoint registers are now implemented * Torque operational data scaling changed from 100 to 10
2.15 | 2024-08-15 | dob | * New alarms (AFE LVRT cannot recover and Drive overload)
2.16 | 2024-08-16 | jml | * slip alarms flags to register sets. ONe set is use to read the alarm state, while the second is used to read the acknowledgement status and send the acknowledgment command. Not implemented yet 2024-08-19
2.17 | 2024-08-21 | jml | * added register address decimal representation
2.18 | 2024-09-18 | dm | * added invalid PIN code alarm to register
2.19 | 2024-10-25 | pb | *added ramps index selection on motor controller setpoints
2.20 | 2024-11-18 | fw | *added magnetizing state to motor controller state
2.21 | 2024-12-19 | dm | *added additional PID operational data registers for output and effective process setpoint
2.22 | 2025-01-06 | mp | *Move PID opdata to 16#0D10
| 2025-06-16 | dob sgh | *added starting state to motor controller state *added new alarm codes (ALARM_CODE_DAMPER_FEEDBACK_LOSS to ALARM_CODE_EMERGENCY_MODE_FORBIDDEN) *Added maintenance mode register *Rename OoS to maintenance mode *Change name of PID state register, description is accurate
2.23 | 2025-06-25 | pb | Fixed MMODE (Maintenance mode) value to match implementation
2.24 | 2025-07-29 | dm | Added IO opdata registers to match requirement.
2.25 | 2025-10-09 | dob | Removed Enable/Disable/Halt/Pause from motor controller commands (MCC)
2.26 | 2025-12-09 | dob | Added new alarm codes (external 1/2/3/4 and motor thermal overload)
2.27 | 2026-02-17 | fw | Added new alarm code for internal MCU comm loss
2.28 | 2026-03-23 | dob | Added new alarm code for BACNet comm loss. This also adds AL6 register.
2.29 | 2026-06-17 | pd | Added analog output status from opData, and added raw values from opData relays.

## Instructions
SmartDrive - Communication Parameters
EXPLANATORY NOTE: This Excel file is for reference only. Refer to the Clean Power VFD
user guide, section about communication, for full information.
The columns include the following criteria:
Code:
Language-independent, this allows a rapid search in the programming manual, which
includes an index of parameter codes.
Profile:
Profile name.
Holding address:
Addresses for Modbus Holding Register
Address for the messaging are in hexadecimal (preceded by 16#) format.
To optimize messaging performance, addresses are given for the control word (MCx) and
the status word (SYSx).
The addresses annotated "speed" are for use in rpm; the addresses annotated "frequency"
are for use in Hz.
Link:
For control word and system word a link is given to their description.
Access:
Read and write options:
R: Read only
W: Write only
R/W: Write, then read
Type:
WORD (Enumeration)
FLAGS (Unsigned)
IEEE754: 32-bit floating point
Unsigned32
Units:
Physical units.
Factory Setting:
Value of the parameter set at the factory.
Range:
Possible values.
Description:
Indicates a description.
Reference:
Gives to the SmartDrive variables document.

## Exception Codes
Code | Name | Description
0x01 | Ilegal function | The function code received in the request is not supported.
0x02 | Illegal data address | The data register address specified in the request is not available for this version of the MODBUS server
0x03 | Illegal data value | The data value specified in the request is not valid.
0x04 | Slave device failure | The MODBUS server was not able to recover
0x06 | Slave device busy

## Device Info (code43)
Device Info
Request for basic information
| Definition |  | Number of Bytes | Value | Comment
| Slave ID |  | 1 | 0x01
| Function code |  | 1 | 0x2B
| Sub-function code |  | 1 | 0x0E
| Product ID |  | 1 | 0x01
| Object Identifier |  | 1 | 0x00
Response for basic information
| Definition |  | Number of Bytes | Value | Comment
| Slave ID |  | 1 | 0x01
| Function code |  | 1 | 0x2B
| Sub-function code |  | 1 | 0x0E
| Product ID |  | 1 | 0x01
| Conformity level |  | 1 | 0x01
| Reserved |  | 1 | 0x00
| Reserved |  | 1 | 0x00
| Number of objects |  | 1 | 0x03
| Object 0: manufacturer name | Object number | 1 | 0x00
|  | Object length | 1 | 0x18
|  | Object content | 24 | SmartD Technologies Inc.
| Object 1: product code | Object number | 1 | 0x01
|  | Object length | 1 | 0x0A (min) | Product code is having variable length.
|  | Object content | 10 (min) | Examples: SDB-1-2185 SDB-1-2185-A | Product code is having variable length.
| Object 2: version number | Object number | 1 | 0x02
|  | Object length | 1 | 0x0B
|  | Object content | 19 | Vxxxx.yy.zz | Example: V2023.11.00
Request for complete information
| Definition |  | Number of Bytes | Value | Comment
| Slave ID |  | 1 | 0x01
| Function code |  | 1 | 0x2B
| Sub-function code |  | 1 | 0x0E
| Product ID |  | 1 | 0x02
| Object Identifier |  | 1 | 0x00
Response for complete information
| Definition |  | Number of Bytes | Value | Comment
| Slave ID |  | 1 | 0x01
| Function code |  | 1 | 0x2B
| Sub-function code |  | 1 | 0x0E
| Product ID |  | 1 | 0x01
| Conformity level |  | 1 | 0x02
| Reserved |  | 1 | 0x00
| Reserved |  | 1 | 0x00
| Number of objects |  | 1 | 0x05
| Object 0: manufacturer name | Object number | 1 | 0x00
|  | Object length | 1 | 0x18
|  | Object content | 24 | SmartD Technologies Inc.
| Object 1: product code | Object number | 1 | 0x01
|  | Object length | 1 | 0x0A (min) | Product code is having variable length.
|  | Object content | 10 (min) | Examples: SDB-1-2185 SDB-1-2185-A | Product code is having variable length.
| Object 2: version number | Object number | 1 | 0x02
|  | Object length | 1 | 0x0B
|  | Object content | 19 | Vxxxx.yy.zz | Example: V2023.11.00
| Object 3: manufacturer URL | Object number | 1 | 0x03
|  | Object length | 1 | 0x13
|  | Object content | 19 | https://smartd.tech
| Object 4: product name | Object number | 1 | 0x04
|  | Object length | 1 | 0x0F
|  | Object content | 15 | Clean Power VFD

## Parameters
ƒ | Service | Name | Holding address | Holding address decimal | IEC61800-7-201 Object | IEC61800-7-201 Name | IEC61800-7-201 Category | Link | Access | Type | Units | Factory setting | Range | Multiplier Factor | Description | Reference
| SmartD Power Meter | OperationalData.line.L1_current | 16#0000 | 0 |  |  |  |  | R | Unsigned16 | A |  | 0.00 ... (depends on drive model) | 100 | Current measured on L1 input line | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.line.L2_current | 16#0001 | 1 |  |  |  |  | R | Unsigned16 | A |  | 0.00 ... (depends on drive model) | 100 | Current measured on L2 input line | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.line.L3_current | 16#0002 | 2 |  |  |  |  | R | Unsigned16 | A |  | 0.00 ... (depends on drive model) | 100 | Current measured on L3 input line | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.line.L12_voltage | 16#0003 | 3 |  |  |  |  | R | Unsigned16 | Vrms |  | 0.00 ... (depends on drive model) | 10 | Voltage between input lines 1 and 2 | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.line.L23_voltage | 16#0004 | 4 |  |  |  |  | R | Unsigned16 | Vrms |  | 0.00 ... (depends on drive model) | 10 | Voltage between input lines 2 and 3 | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.line.L31_voltage | 16#0005 | 5 |  |  |  |  | R | Unsigned16 | Vrms |  | 0.00 ... (depends on drive model) | 10 | Voltage between input lines 1 and 3 | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.line.frequency | 16#0006 | 6 |  |  |  |  | R | Unsigned16 | Hz |  | 0.00 ... 100.00 | 100 | Frequency of the signal measured on the input lines L1/L2/L3. | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.line.real_power | 16#0007 | 7 |  |  |  |  | R | Signed16 | Watts |  | 0.00 ... 100,000.00 | 0.01 | The actual amount of power being used, or dissipated by the drive and the motor attached to the drive. | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.line.apparent_power | 16#0008 | 8 |  |  |  |  | R | Signed16 | VA |  | 0.00 ... 100,000.00 | 0.01 | Apparent power is the power the grid must be able to withstand at the current moment to power the drive and the motor controlled by this drive. | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.line.reactive_power | 16#0009 | 9 |  |  |  |  | R | Signed16 | VAR |  | -100,000.00 ... 100,0000.00 | 0.01 | Reactive power represents electrical energy stored in the drive coils and motor that then flows back to the grid. | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.line.power_factor | 16#000A | 10 |  |  |  |  | R | Signed16 |  |  | -1.00 ... 1.00 | 100 | The power factor is defined as the ratio of the real power absorbed by the drive and its load to the apparent power flowing in the drive. | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.motor.U_current | 16#0100 | 256 |  |  |  |  | R | Unsigned16 | A |  | 0.00 ... (depends on drive model) | 100 | Current measured on U output line | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.motor.V_current | 16#0101 | 257 |  |  |  |  | R | Unsigned16 | A |  | 0.00 ... (depends on drive model) | 100 | Current measured on V output line | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.motor.W_current | 16#0102 | 258 |  |  |  |  | R | Unsigned16 | A |  | 0.00 ... (depends on drive model) | 100 | Current measured on W output line | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.motor.UV_voltage | 16#0103 | 259 |  |  |  |  | R | Unsigned16 | Vrms |  | 0.00 ... (depends on drive model) | 10 | Voltage between output lines U and V | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.motor.VW_voltage | 16#0104 | 260 |  |  |  |  | R | Unsigned16 | Vrms |  | 0.00 ... (depends on drive model) | 10 | Voltage between output lines V and W | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.motor.WU_voltage | 16#0105 | 261 |  |  |  |  | R | Unsigned16 | Vrms |  | 0.00 ... (depends on drive model) | 10 | Voltage between output lines U and W | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.motor.frequency | 16#0106 | 262 |  |  |  |  | R | Unsigned16 | Hz |  | 0.00 ... 120.00 | 100 | Frequency of signal the outputed on lines U/V/W. | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.motor.balance | 16#0107 | 263 |  |  |  |  | R | Unsigned16 | % |  | 0.00 ... 1.00 | 100 | The motor is considered balanced if the voltages, currents and power factors in all three phases are identical. Conversely, when any of these parameters are not identical the circuit is classified as unbalanced. | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.motor.real_power | 16#0108 | 264 |  |  |  |  | R | Signed16 | Watts |  | 0.00 ... 100,000.00 | 0.01 | The actual amount of power being used, or dissipated by the motor (and other loads) attached to the drive. | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.motor.apparent_power | 16#0109 | 265 |  |  |  |  | R | Signed16 | VA |  | 0.00 ... 100,000.00 | 0.01 | Apparent power is the power the drive must be able to withstand at the current moment to power the motor and other loads controlled by this drive. | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.motor.reactive_power | 16#010A | 266 |  |  |  |  | R | Signed16 | VAR |  | -100,000.00 ... 100,000.00 | 0.01 | Reactive power represents electrical energy stored in the drive coils and motor that then flows back to the grid. | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.motor.power_factor | 16#010B | 267 |  |  |  |  | R | Signed16 |  |  | -1.00 ... 1.00 | 100 | The power factor is defined as the ratio of the real power absorbed by the drive and its load to the apparent power flowing to motor (and other loads). | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.dcbus.Vdc_plus_voltage | 16#0200 | 512 |  |  |  |  | R | Unsigned16 | V |  | 0.00 ... 1,000.00 | 10 | Votlage measure on postive side of the internal DC bus of the drive. | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.dcbus.Vdc_minus_voltage | 16#0201 | 513 |  |  |  |  | R | Unsigned16 | V |  | 0.00 ... 1,000.00 | 10 | Votlage measure on postive side of the internal DC bus of the drive. | SmartDrive Variables - power_meter
| SmartD Motor Controller | OperationalData.motor_state | 16#0400 | 1024 |  |  |  | MCS | R | WORD (Enumeration) |  |  |  |  | State of the motor. | SmartDrive Variables - motor_controller
| SmartD Motor Controller | OperationalData.direction | 16#0401 | 1025 |  |  |  | MCD | R | WORD (Enumeration) |  |  |  |  | Rotation direction of the shaft. | SmartDrive Variables - motor_controller
| SmartD Motor Controller | OperationalData.frequency | 16#0402 | 1026 |  |  |  |  | R | Unsigned16 | Hz |  | 0.0 .. 120.0 | 100 | Current motor synchronous speed. | SmartDrive Variables - motor_controller
| SmartD Motor Controller | OperationalData.velocity | 16#0403 | 1027 |  |  |  |  | R | Unsigned16 | rpm |  | 0 .. 7200 | 1 | Current motor synchronous speed. | SmartDrive Variables - motor_controller
| SmartD Motor Controller | OperationalData.mode | 16#0404 | 1028 |  |  |  | MCM | R | WORD (Enumeration) |  |  |  |  | Motor operation mode
| SmartD Motor Controller | OperationalData.torque | 16#0405 | 1029 |  |  |  |  | R | Signed16 | % |  | -500 .. 500 | 10 | Current estimated motor torque
| SmartD Motor Controller | SetPoints.command | 16#0410 | 1040 |  |  |  | MCC | R/W | WORD (Enumeration) |  |  |  |  | Requested state of the output inverter of the drive. | SmartDrive Variables - motor_controller
| SmartD Motor Controller | SetPoints.direction | 16#0411 | 1041 |  |  |  | MCD | R/W | WORD (Enumeration) |  |  |  |  | Rotation direction of the shaf. | SmartDrive Variables - motor_controller
| SmartD Motor Controller | SetPoints.frequency | 16#0412 | 1042 |  |  |  |  | R/W | Unsigned16 | Hz |  | 0.0 .. 120.0 | 100 | Desired motor synchronous speed. | SmartDrive Variables - motor_controller
| SmartD Motor Controller | SetPoints.presetFrequency | 16#0413 | 1043 |  |  |  |  | R/W | Unsigned16 |  |  | 0 .. 7 | 1 | Get or set the preset frequency index | SmartDrive Variables - motor_controller
| SmartD Motor Controller | SetPoints.velocity | 16#0414 | 1044 |  |  |  |  | R/W | Unsigned16 | rpm |  | 0 .. 7200 | 1 | Desired motor shaft velocity | SmartDrive Variables - motor_controller
| SmartD Motor Controller | SetPoints.presetVelocity | 16#0415 | 1045 |  |  |  |  | R/W | Unsigned16 |  |  | 0 .. 7 | 1 | Get or set the preset velocity index | SmartDrive Variables - motor_controller
| SmartD Motor Controller | SetPoints.torque | 16#0416 | 1046 |  |  |  |  | R/W | Signed16 | % |  | -500 .. 500 | 10 | Desired motor torque | SmartDrive Variables - motor_controller
N/A | SmartD Motor Controller | [DEPRECATED] SetPoints.presetTorque | 16#0417 | 1047 |  |  |  |  | R/W | Unsigned16 |  |  | 0 .. 7 | 1 | Get or set the preset torque index | SmartDrive Variables - motor_controller
| SmartD Motor Controller | SetPoints.mode | 16#0418 | 1048 |  |  |  | MCM | R/W | WORD (Enumeration)
| SmartD Motor Controller | SetPoints.minTorque | 16#0419 | 1049 |  |  |  |  | R/W | Signed16 | % |  | -500..500 | 10 | Set the largest amount of torque that can be applied to the motor
| SmartD Motor Controller | SetPoints.maxTorque | 16#041A | 1050 |  |  |  |  | R/W | Signed16 | % |  | -500..500 | 10 | Set the smallest amount of torque that can be applied to the motor
| SmartD Motor Controller | SetPoints.rampUpCurveIndex | 16#041B | 1051 |  |  |  |  | R/W | Unsigned16 |  |  | 0 .. 3 | 1 | Get or set the ramp up curve index | SmartDrive Variables - motor_controller
| SmartD Motor Controller | SetPoints.rampDownCurveIndex | 16#041C | 1052 |  |  |  |  | R/W | Unsigned16 |  |  | 0 .. 3 | 1 | Get or set the ramp down curve index | SmartDrive Variables - motor_controller
N/A | SmartD Motor Controller | Configuration.motorNameplate.nominalInputFrequency | 16#0460 | 1120 |  |  |  |  | R | Unsigned16 | Hz |  | 50 or 60 | 100 | Nominal motor frequency
N/A | SmartD Motor Controller | Configuration.motorNameplate.nominalVelocity | 16#0461 | 1121 |  |  |  |  | R | Unsigned16 | rpm |  | 0 .. 7200 | 10 | Nominal motor shaft speed
N/A | SmartD Motor Controller | Configuration.motorNameplate.nominalVoltage | 16#0462 | 1122 |  |  |  |  | R | Unsigned16 | Vrms |  | 0 ... (480 or 600 depends on drive model) | 100 | Nominal motor voltage
N/A | SmartD Motor Controller | Configuration.motorNameplate.nominalCurrent | 16#0463 | 1123 |  |  |  |  | R | Unsigned16 | A |  | 0 ... (depends on drive model) | 100 | Moninal motor current (FLA)
N/A | SmartD Motor Controller | Configuration.motorNameplate.minInputFrequency | 16#0464 | 1124 |  |  |  |  | R | Unsigned16 | Hz |  | 0 .. 119 | 100 | Minimum motor frequency
N/A | SmartD Motor Controller | Configuration.motorNameplate.maxInputFrequency | 16#0465 | 1125 |  |  |  |  | R | Unsigned16 | Hz |  | 1 .. 120 | 100 | Maximum motor frequency
| SmartD Motor Controller | Metrics.lifeTime.startCountLowWord | 16#0500 | 1280 |  |  |  |  | R | Unsigned16 |  | 0 | 0 .. 65535 | 1 | Number of times the VFD has been started starting a motor in whole lifetime (bit 15..0) of a 32-bit counter
| SmartD Motor Controller | Metrics.lifeTime.startCountHighWord | 16#0501 | 1281 |  |  |  |  | R | Unsigned16 |  | 0 | 0 .. 65535 | 1 | Number of times the VFD has been started starting a motor in whole lifetime (bit 31..16) of a 32-bit counter
| SmartD Motor Controller | Metrics.lifeTime.runTimeLowWord | 16#0502 | 1282 |  |  |  |  | R | Unsigned16 | Hours | 0 | 0 .. 65535 | 1 | Cumulative time the VFD has been running a motor in whole lifetime (bit 15..0) of a 32-bit counter
| SmartD Motor Controller | Metrics.lifeTime.runTimeHighWord | 16#0503 | 1283 |  |  |  |  | R | Unsigned16 | Hours | 0 | 0 .. 65535 | 1 | Cumulative time the VFD has been running a motor in whole lifetime (bit 31..16) of a 32-bit counter
| SmartD Motor Controller | Metrics.runTime.startCountLowWord | 16#0504 | 1284 |  |  |  |  | R | Unsigned16 |  | 0 | 0 .. 65535 | 1 | Number of times the motor has been started (bit 15..0) of a 32-bit counter - could be reset when the user replace the motor
| SmartD Motor Controller | Metrics.runTime.startCountHighWord | 16#0505 | 1285 |  |  |  |  | R | Unsigned16 |  | 0 | 0 .. 65535 | 1 | Number of times the motor has been started (bit 31..16) of a 32-bit counter - could be reset when the user replace the motor
| SmartD Motor Controller | Metrics.runTime.runTimeLowWord | 16#0506 | 1286 |  |  |  |  | R | Unsigned16 | Hours | 0 | 0 .. 65535 | 1 | Cumulative motor runtime (bit 15..0) of a 32-bit counter - could be reset when the user replace the motor
| SmartD Motor Controller | Metrics.runTime.runTimeHighWord | 16#0507 | 1287 |  |  |  |  | R | Unsigned16 | Hours | 0 | 0 .. 65535 | 1 | Cumulative motor has been started (bit 31..16) of a 32-bit counter - could be reset when the user replace the motor
| SmartD Motor Controller | Metrics.MotorLifeTime.startCountLowWord | 16#0508 | 1288 |  |  |  |  | R | Unsigned16 |  | 0 | 0 .. 65535 | 1 | Number of times the Motor has been started (bit 15..0) of a 32-bit counter - can be reset when motor is replaces
| SmartD Motor Controller | Metrics.MotorLifeTime.startCountHighWord | 16#0509 | 1289 |  |  |  |  | R | Unsigned16 |  | 0 | 0 .. 65535 | 1 | Number of times the Motor has been started (bit 31..16) of a 32-bit counter - can be reset when motor is replaces
| SmartD Motor Controller | Metrics.MotorLifeTime.runTimeLowWord | 16#050A | 1290 |  |  |  |  | R | Unsigned16 | Hours | 0 | 0 .. 65535 | 1 | Cumulative VFD runtime (bit 15..0) of a 32-bit counter - can be reset when motor is replaces
| SmartD Motor Controller | Metrics.MotorLifeTime.runTimeHighWord | 16#050B | 1291 |  |  |  |  | R | Unsigned16 | Hours | 0 | 0 .. 65535 | 1 | Cumulative VFD runtime (bit 31..16) of a 32-bit counter - can be reset when motor is replaces
| SmartD Motor Controller | Metrics.MotorRunTime.runTimeLowWord | 16#050C | 1292 |  |  |  |  | R | Unsigned16 | Hours | 0 | 0 .. 65535 | 1 | motor runtime since its last start (bit 15..0) of a 32-bit counter
| SmartD Motor Controller | Metrics.MotorRunTime.runTimeHighWord | 16#050D | 1293 |  |  |  |  | R | Unsigned16 | Hours | 0 | 0 .. 65535 | 1 | motor runtime since its last start (bit 31..16) of a 32-bit counter
| SmartD Cooling Management | OperationalData.driveTemperature | 16#0600 | 1536 |  |  |  |  | R | Signed16 | Degree C |  | -20.0 .. 140.0 | 10 | Drive power electronic temperature.
| SmartD Cooling Management | OperationalData.driveAmbiantTemperature | 16#0601 | 1537 |  |  |  |  | R | Signed16 | Degree C |  | -20.0 .. 140.0 | 10 | Drive internal temperature. Ususaly lower than OperationalData.drive_temperature
| SmartD Cooling Management | OperationalData.fanCount | 16#0602 | 1538 |  |  |  |  | R | Unsigned16 | rpm |  | 1 .. 4 | 1 | Number of fans available on this
| SmartD Cooling Management | OperationalData.fans[0].speed | 16#0603 | 1539 |  |  |  |  | R | Unsigned16 | rpm |  | 0 .. 65535 | 1 | Fan#1 speed in RPM
| SmartD Cooling Management | OperationalData.fans[1].speed | 16#0604 | 1540 |  |  |  |  | R | Unsigned16 | rpm |  | 0 .. 65535 | 1 | Fan#1 speed in RPM
| SmartD Cooling Management | OperationalData.fans[2].speed | 16#0605 | 1541 |  |  |  |  | R | Unsigned16 | rpm |  | 0 .. 65535 | 1 | Fan#1 speed in RPM
| SmartD Cooling Management | OperationalData.fans[3].speed | 16#0606 | 1542 |  |  |  |  | R | Unsigned16 | rpm |  | 0 .. 65535 | 1 | Fan#1 speed in RPM
| SmartD Cooling Management | Metrics.fans[0].Runtime LowWord | 16#0640 | 1600 |  |  |  |  | R | Unsigned16 | Hours |  | 0 .. 65535 | 1 | Number of times the Fan has been running since last metrics reset (bit 15..0) of a 32-bit counter
| SmartD Cooling Management | Metrics.fans[0].Runtime HighWord | 16#0641 | 1601 |  |  |  |  | R | Unsigned16 | Hours |  | 0 .. 65535 | 1 | Number of times the Fan has been running since last metrics reset (bit 31..16) of a 32-bit counter
| SmartD Cooling Management | Metrics.fans[0].TotalLifeExpectancy LowWord | 16#0642 | 1602 |  |  |  |  | R | Unsigned16 | Hours |  | 0 .. 65535 | 1 | Total fan life expectancy in second (bit 15..0) of a 32-bit counter
| SmartD Cooling Management | Metrics.fans[0].TotalLifeExpectancy HighWord | 16#0643 | 1603 |  |  |  |  | R | Unsigned16 | Hours |  | 0 .. 65535 | 1 | Total fan life expectancy in second (bit 31..16) of a 32-bit counter
| SmartD Cooling Management | Metrics.fans[0].RemainingLifeExpectancy LowWord | 16#0644 | 1604 |  |  |  |  | R | Unsigned16 | Hours |  | 0 .. 65535 | 1 | Remaining fan life expectancy in second (bit 15..0) of a 32-bit counter
| SmartD Cooling Management | Metrics.fans[0].RemainingLifeExpectancy HighWord | 16#0645 | 1605 |  |  |  |  | R | Unsigned16 | Hours |  | 0 .. 65535 | 1 | Remaining fan life expectancy in second (bit 31..16) of a 32-bit counter
| SmartD Cooling Management | Metrics.fans[1].Runtime LowWord | 16#0646 | 1606 |  |  |  |  | R | Unsigned16 | Hours |  | 0 .. 65535 | 1 | Number of times the Fan has been running since last metrics reset (bit 15..0) of a 32-bit counter
| SmartD Cooling Management | Metrics.fans[1].Runtime HighWord | 16#0647 | 1607 |  |  |  |  | R | Unsigned16 | Hours |  | 0 .. 65535 | 1 | Number of times the Fan has been running since last metrics reset (bit 31..16) of a 32-bit counter
| SmartD Cooling Management | Metrics.fans[1].TotalLifeExpectancy LowWord | 16#0648 | 1608 |  |  |  |  | R | Unsigned16 | Hours |  | 0 .. 65535 | 1 | Total fan life expectancy in second (bit 15..0) of a 32-bit counter
| SmartD Cooling Management | Metrics.fans[1].TotalLifeExpectancy HighWord | 16#0649 | 1609 |  |  |  |  | R | Unsigned16 | Hours |  | 0 .. 65535 | 1 | Total fan life expectancy in second (bit 31..16) of a 32-bit counter
| SmartD Cooling Management | Metrics.fans[1].RemainingLifeExpectancy LowWord | 16#064A | 1610 |  |  |  |  | R | Unsigned16 | Hours |  | 0 .. 65535 | 1 | Remaining fan life expectancy in second (bit 15..0) of a 32-bit counter
| SmartD Cooling Management | Metrics.fans[1].RemainingLifeExpectancy HighWord | 16#064B | 1611 |  |  |  |  | R | Unsigned16 | Hours |  | 0 .. 65535 | 1 | Remaining fan life expectancy in second (bit 31..16) of a 32-bit counter
| SmartD Cooling Management | Metrics.fans[2].Runtime LowWord | 16#064C | 1612 |  |  |  |  | R | Unsigned16 | Hours |  | 0 .. 65535 | 1 | Number of times the Fan has been running since last metrics reset (bit 15..0) of a 32-bit counter
| SmartD Cooling Management | Metrics.fans[2].Runtime HighWord | 16#064D | 1613 |  |  |  |  | R | Unsigned16 | Hours |  | 0 .. 65535 | 1 | Number of times the Fan has been running since last metrics reset (bit 31..16) of a 32-bit counter
| SmartD Cooling Management | Metrics.fans[2].TotalLifeExpectancy LowWord | 16#064E | 1614 |  |  |  |  | R | Unsigned16 | Hours |  | 0 .. 65535 | 1 | Total fan life expectancy in second (bit 15..0) of a 32-bit counter
| SmartD Cooling Management | Metrics.fans[2].TotalLifeExpectancy HighWord | 16#064F | 1615 |  |  |  |  | R | Unsigned16 | Hours |  | 0 .. 65535 | 1 | Total fan life expectancy in second (bit 31..16) of a 32-bit counter
| SmartD Cooling Management | Metrics.fans[2].RemainingLifeExpectancy LowWord | 16#0651 | 1617 |  |  |  |  | R | Unsigned16 | Hours |  | 0 .. 65535 | 1 | Remaining fan life expectancy in second (bit 15..0) of a 32-bit counter
| SmartD Cooling Management | Metrics.fans[2].RemainingLifeExpectancy HighWord | 16#0652 | 1618 |  |  |  |  | R | Unsigned16 | Hours |  | 0 .. 65535 | 1 | Remaining fan life expectancy in second (bit 31..16) of a 32-bit counter
| SmartD Cooling Management | Metrics.fans[3].Runtime LowWord | 16#0653 | 1619 |  |  |  |  | R | Unsigned16 | Hours |  | 0 .. 65535 | 1 | Number of times the Fan has been running since last metrics reset (bit 15..0) of a 32-bit counter
| SmartD Cooling Management | Metrics.fans[3].Runtime HighWord | 16#0654 | 1620 |  |  |  |  | R | Unsigned16 | Hours |  | 0 .. 65535 | 1 | Number of times the Fan has been running since last metrics reset (bit 31..16) of a 32-bit counter
| SmartD Cooling Management | Metrics.fans[3].TotalLifeExpectancy LowWord | 16#0655 | 1621 |  |  |  |  | R | Unsigned16 | Hours |  | 0 .. 65535 | 1 | Total fan life expectancy in second (bit 15..0) of a 32-bit counter
| SmartD Cooling Management | Metrics.fans[3].TotalLifeExpectancy HighWord | 16#0656 | 1622 |  |  |  |  | R | Unsigned16 | Hours |  | 0 .. 65535 | 1 | Total fan life expectancy in second (bit 31..16) of a 32-bit counter
| SmartD Cooling Management | Metrics.fans[3].RemainingLifeExpectancy LowWord | 16#0657 | 1623 |  |  |  |  | R | Unsigned16 | Hours |  | 0 .. 65535 | 1 | Remaining fan life expectancy in second (bit 15..0) of a 32-bit counter
| SmartD Cooling Management | Metrics.fans[3].RemainingLifeExpectancy HighWord | 16#0658 | 1624 |  |  |  |  | R | Unsigned16 | Hours |  | 0 .. 65535 | 1 | Remaining fan life expectancy in second (bit 31..16) of a 32-bit counter
| SmartD System | OperationalData.system_state | 16#0800 | 2048 |  |  |  | SYS | R | WORD (Enumeration) |  |  |  |  | System state. | SmartDrive Variables - system
| SmartD System | ResetLockout | 16#0840 | 2112 |  |  |  | SYSR | W | WORD (Enumeration) |  |  |  |  | System state reset. | SmartDrive Variables - system
| SmartD System | Setpoint.systemMaintenanceMode | 16#0841 | 2113 |  |  |  | MMODE | W | WORD (Enumeration) |  |  |  |  | 1=enable, 2=disable
| SmartD System | SetPoints.remoteControlMode | 16#0900 | 2304 |  |  |  | SYSRC | R/W | WORD (Enumeration) |  |  |  |  | Select local vs remote control | SmartDrive Variables - motor_controller
| SmartD System | SetPoints.remoteControlSource | 16#0901 | 2305 |  |  |  | SYSRCS | R/W | WORD (Enumeration) |  |  | 0 - 2 | 1 | Select remote source 1 or 2, 0 unspecified | SmartDrive Variables - motor_controller
| SmartD System | Metrics.lifeTime.startCountLowWord | 16#0920 | 2336 |  |  |  |  | R | Unsigned16 |  | 0 | 0 .. 65535 | 1 | Number of times the VFD has been started in whole lifetime (bit 15..0) of a 32-bit counter
| SmartD System | Metrics.lifeTime.startCountHighWord | 16#0921 | 2337 |  |  |  |  | R | Unsigned16 |  | 0 | 0 .. 65535 | 1 | Number of times the VFD has been started in whole lifetime (bit 31..16) of a 32-bit counter
| SmartD System | Metrics.lifeTime.runTimeLowWord | 16#0922 | 2338 |  |  |  |  | R | Unsigned16 | Hours | 0 | 0 .. 65535 | 1 | Cumulative time the VFD has been powered in whole lifetime (bit 15..0) of a 32-bit counter
| SmartD System | Metrics.lifeTime.runTimeHighWord | 16#0923 | 2339 |  |  |  |  | R | Unsigned16 | Hours | 0 | 0 .. 65535 | 1 | Cumulative time the VFD has been powered in whole lifetime (bit 31..16) of a 32-bit counter
| SmartD System | Metrics.UpTime.UpTimeLowWord | 16#0924 | 2340 |  |  |  |  | R | Unsigned16 | Hours | 0 | 0 .. 65535 | 1 | Time the VFD has been powered on since last boot (bit 15..0) of a 32-bit counter
| SmartD System | Metrics.UpTime.UpTimeHighWord | 16#0925 | 2341 |  |  |  |  | R | Unsigned16 | Hours | 0 | 0 .. 65535 | 1 | Time the VFD has been powered on since last boot (bit 31..16) of a 32-bit counter
| SmartD I/Os | Configuration.AnalogInput1.Mode | 16#0940 | 2368 |  |  |  | AIMOD | R | BitField |  |  |  |  | 4 LSB bits for mode. AI1 configuration mode (voltage, current, impedance, PTC) 12 other bits RFU
| SmartD I/Os | Configuration.AnalogInput2.Mode | 16#0941 | 2369 |  |  |  | AIMOD | R | BitField |  |  |  |  | 4 LSB bits for mode. AI2 configuration mode (voltage, current, impedance, PTC) 12 other bits RFU
| SmartD I/Os | Configuration.AnalogInput3.Mode | 16#0942 | 2370 |  |  |  | AIMOD | R | BitField |  |  |  |  | 4 LSB bits for mode. AI3 configuration mode (voltage, current, impedance, PTC) 12 other bits RFU
| SmartD I/Os | OperationalData.analogInput1.Raw | 16#0950 | 2384 |  |  |  |  | R | Signed16 |  |  | 0 - 20 000 | 1000 | AI1 Raw value in configured units, scaled. For example, read 20 000 in current mode = 20.0 mA on analog input 1. Units are mA for current, volts for voltage, kOhm for impedance and PTC.
| SmartD I/Os | OperationalData.analogInput2.Raw | 16#0951 | 2385 |  |  |  |  | R | Signed16 |  |  | 0 - 20 000 | 1000 | AI2 Raw value in configured units, scaled. For example, read 20 000 in current mode = 20.0 mA on analog input 2. Units are mA for current, volts for voltage, kOhm for impedance and PTC.
| SmartD I/Os | OperationalData.analogInput3.Raw | 16#0952 | 2386 |  |  |  |  | R | Signed16 |  |  | 0 - 20 000 | 1000 | AI3 Raw value in configured units, scaled. For example, read 20 000 in current mode = 20.0 mA on analog input 3. Units are mA for current, volts for voltage, kOhm for impedance and PTC.
| SmartD I/Os | OperationalData.analogInput1.Standardized | 16#0960 | 2400 |  |  |  |  | R | Signed16 |  |  | 0 - 32 767 |  | AI1 value standardized to signed int16. In current mode, range 0-20mA is mapped to range 0-32767. For Volt mode, range 0-10 is mapped to 0-32767, For resistive mode, range 0-10000 is mapped to 0-32767
| SmartD I/Os | OperationalData.analogInput2.Standardized | 16#0961 | 2401 |  |  |  |  | R | Signed16 |  |  | 0 - 32 767 |  | AI2 value standardized to signed int16. In current mode, range 0-20mA is mapped to range 0-32767. For Volt mode, range 0-10 is mapped to 0-32767, For resistive mode, range 0-10000 is mapped to 0-32767
| SmartD I/Os | OperationalData.analogInput3.Standardized | 16#0962 | 2402 |  |  |  |  | R | Signed16 |  |  | 0 - 32 767 |  | AI3 value standardized to signed int16. In current mode, range 0-20mA is mapped to range 0-32767. For Volt mode, range 0-10 is mapped to 0-32767, For resistive mode, range 0-10000 is mapped to 0-32767
| SmartD I/Os | Configuration.analogOutput1.Mode | 16#0970 | 2416 |  |  |  |  | R | BitField |  |  |  |  | 4 LSB bits for mode. AO1 configuration mode (unspecified is 0, current is 1, voltage is 2) 12 other bits RFU
| SmartD I/Os | Configuration.analogOutput2.Mode | 16#0971 | 2417 |  |  |  |  | R | BitField |  |  |  |  | 4 LSB bits for mode. AO2 configuration mode (unspecified is 0, current is 1, voltage is 2) 12 other bits RFU
| SmartD I/Os | OperationalData.analogOutput1.Raw | 16#0978 | 2424 |  |  |  |  | R | Signed16 |  |  | 0 - 20 000 | 1000 | AO1 Raw value in configured units, scaled. For example, read 20 000 in current mode = 20.0 mA on analog output 1. Units are mA for current and volts for voltage.
| SmartD I/Os | OperationalData.analogOutput2.Raw | 16#0979 | 2425 |  |  |  |  | R | Signed16 |  |  | 0 - 20 000 | 1000 | AO2 Raw value in configured units, scaled. For example, read 20 000 in current mode = 20.0 mA on analog output 2. Units are mA for current and volts for voltage.
| SmartD I/Os | OperationalData.analogOutput1.Standardized | 16#0980 | 2432 |  |  |  |  | R | Signed16 |  |  | 0 - 32 767 |  | AO1 value standardized to signed int16. In current mode, range 0-20mA is mapped to range 0-32767. For Volt mode, range 0-10 is mapped to 0-32767
| SmartD I/Os | OperationalData.analogOutput2.Standardized | 16#0981 | 2433 |  |  |  |  | R | Signed16 |  |  | 0 - 32 767 |  | AO1 value standardized to signed int16. In current mode, range 0-20mA is mapped to range 0-32767. For Volt mode, range 0-10 is mapped to 0-32767
N/A | SmartD I/Os | Configuration.digitalInputs.Polarity | 16#0990 | 2448 |  |  |  |  | R | Unsigned16
N/A | SmartD I/Os | Configuration.relays.Polarity | 16#0992 | 2450 |  |  |  |  | R | Unsigned16 |  |  |  |  | bit 0 = relay 1, bit 1 relay 2, bit 2 relay 3. bit to 0 = de-energized by default, bit to 1 = energized by default
| SmartD I/Os | OperationalData.digitalInputs | 16#09A0 | 2464 |  |  |  | DIS | R | FLAGS (Unsigned16) |  |  |  |  | State of the digital intputs. Read 1 in bit position = active. Read 0 = inactive, uncofingured, or configured for encoder.
N/A | SmartD I/Os | OperationalData.relays | 16#09A2 | 2466 |  |  |  | RELAYS | R | FLAGS (Unsigned16) |  |  |  |  | State of the relays, in form of a bif field with Relay 1 = bit 0, relay2 = bit 1, relay 3 = bit 2
New | SmartD Alarms | OperationalData,.activeFlags #1 | 16#0C00 | 3072 |  |  |  | AL1 | R | FLAGS (Unsigned16) |  |  |  |  | Read: Alarm flags. | SmartDrive Variables - alarms
New | SmartD Alarms | OperationalData.activeFlags #2 | 16#0C01 | 3073 |  |  |  | AL2 | R | FLAGS (Unsigned16) |  |  |  |  | Read: Alarm flags. | SmartDrive Variables - alarms
New | SmartD Alarms | OperationalData.activeFlags #3 | 16#0C02 | 3074 |  |  |  | AL3 | R | FLAGS (Unsigned16) |  |  |  |  | Read: Alarm flags. | SmartDrive Variables - alarms
New | SmartD Alarms | OperationalDats.activeFlags #4 | 16#0C03 | 3075 |  |  |  | AL4 | R | FLAGS (Unsigned16) |  |  |  |  | Read: Alarm flags. | SmartDrive Variables - alarms
New | SmartD Alarms | OperationalDats.activeFlags #5 | 16#0C04 | 3076 |  |  |  | AL5 | R | FLAGS (Unsigned16) |  |  |  |  | Read: Alarm flags. | SmartDrive Variables - alarms
N/A | SmartD Alarms | OperationalData.needAckFlags #1 (R) SetPoints.resetNeedAckFlags #1 (W) | 16#0C20 | 3104 |  |  |  | AL1 | R/W | FLAGS (Unsigned16) |  |  |  |  | Read: Arm flags. Write: Alarm acks. | SmartDrive Variables - alarms
N/A | SmartD Alarms | OperationalData.needAckFlags #2 (R) SetPoints.resetNeedAckFlags #2 (W) | 16#0C21 | 3105 |  |  |  | AL2 | R/W | FLAGS (Unsigned16) |  |  |  |  | Read: Arm flags. Write: Alarm acks. | SmartDrive Variables - alarms
N/A | SmartD Alarms | OperationalData.needAckFlags #3 (R) SetPoints.resetNeedAckFlags #3 (W) | 16#0C22 | 3106 |  |  |  | AL3 | R/W | FLAGS (Unsigned16) |  |  |  |  | Read: Arm flags. Write: Alarm acks. | SmartDrive Variables - alarms
N/A | SmartD Alarms | OperationalData.needAckFlags #4 (R) SetPoints.resetNeedAckFlags #4 (W) | 16#0C23 | 3107 |  |  |  | AL4 | R/W | FLAGS (Unsigned16) |  |  |  |  | Read: Arm flags. Write: Alarm acks. | SmartDrive Variables - alarms
N/A | SmartD Alarms | OperationalData.needAckFlags #5 (R) SetPoints.resetNeedAckFlags #5 (W) | 16#0C24 | 3108 |  |  |  | AL5 | R/W | FLAGS (Unsigned16) |  |  |  |  | Read: Arm flags. Write: Alarm acks. | SmartDrive Variables - alarms
| SmartD PID#1 | Reserved | 16#0D00 | 3328 |  |  |  |  | R
| SmartD PID#1 | SetPoints.desiredProcessValue | 16#0D01 | 3329 |  |  |  |  | R/W | Unsigned16 | % |  | 0.. 100 | 100 | Read/Write the desired process setpoint value of PID index 1. % relative to PID1 setpoint range configuration. Values above maximum saturate to maximum value. Values below minimum throw exception
| SmartD PID#1 | SetPoints.outputMode | 16#0D02 | 3330 |  |  |  | PIDOM | R/W | WORD (Enumeration) |  |  |  |  | Read/Write PID index 1: Select Output Mode
| SmartD PID#1 | SetPoints.forcedOutputValueFrequency | 16#0D03 | 3331 |  |  |  |  | R/W | Unsigned16 | Hz |  | 0.0 .. 120.0 | 100 | Read/Write the forced output value in frequecy (Hz). Read returns 0 and Write is ignored, if Clean Power VFD is not configured to use frequency (hz).
| SmartD PID#1 | SetPoints.forcedOutputValueVelocity | 16#0D04 | 3332 |  |  |  |  | R/W | Unsigned16 | rpm |  | 0 .. 7200 | 1 | Read/Write the force output value in velocity (rpm). Read returns 0 and Write is ignored, if Clean Power VFD is not configured to use velocity (rpm).
New | SmartD PID#1 | OperationalData.feedbackValue | 16#0D10 | 3344 |  |  |  |  | R | Signed16 | % |  | -250 .. 250 (support overshoot) | 100 | Read the process value of PID index 1. % relative to PID1 setpoint range configuration. Values outside range saturate to min/max
N/A | SmartD PID#1 | OperationalData.outputFrequency | 16#0D11 | 3345 |  |  |  |  | R | Unsigned16 | Hz |  | 0.0 .. 120.0 | 1 | Read the output of PID index 1 to the motor in Hz
N/A | SmartD PID#1 |  | 16#0D12 | 3346 |  |  |  |  | R | Unsigned16 | rpm |  | 0 .. 7200 |  | Read the output of PID index 1 to the motor in rpm
N/A | SmartD PID#1 | OperationalData.effectiveProcessSetpoint | 16#0D13 | 3347 |  |  |  |  | R | Signed16 | rpm |  | 0.. 100 | 1 | Read the effective setpoint of PID at index 1
New | SmartD PID#1 | OperationalData.pidState | 16#0D14 | 3348 |  |  |  | PIDPS | R | Unsigned16
New | SmartD PID#1 | Configuration.ActiveProfileID | 16#0E00 | 3584 |  |  |  |  | R/W | WORD (Enumeration) |  |  |  |  | Get or set the active configuration profile
| SmartD MODBUS | Profile Version | 16#FF00 | 65280 |  |  |  | MBPV | R | BITFIELD (Unsigned16) |  | 16#0211 |  |  | MODBUS Profile version minor
| SmartD MODBUS | Reserved | 16#FF01 | 65281 |  |  |  |  | R | Unsigned16 |  |  |  |  | Reserved
| SmartD MODBUS | Profile ID | 16#FF02 | 65282 |  |  |  | MBPID | R | WORD (Enumeration) |  | 16#0000 |  |  | List of profile must be defined lateer.
| SmartD MODBUS | Heartbeat | 16#FF03 | 65283 |  |  |  |  | R/W | Unsigned16 |  | 16#0000 |  |  | Read: obtain the counter value of the heartbeat register and reset the comm loss alarm watchdog. Write: reset the comm loss alarm watchdog.
Legend
Implemented
N/A | Not implemented
New | New implementation
Updared by dev team each we modify this document

## Enumerations
List ID | Value | Display | Description
MCS | 0 | Unspecified
| 1 | Disabled | Motor is halted and command ON is forbidden.
| 2 | Halted | Motor is halted.
| 3 | Ramping Up | Motor is ramping up.
| 4 | Running | Motor is running in steady state.
| 5 | Ramping Down | Motor is ramping down.
| 6 | Autotuning | Motor has autotuning in progress.
| 7 | Paused | Motor is still active, but not turning. Will start turning again on a motor speed change command
| 8 | Magnetizing | Motor is in the pre-magnetizing state.
| 9 | Starting | Motor is waiting for the start sequence to finish (ex: bypass relay is being enabled and AFE is starting).
MCD | 0 | Unspecified
| 1 | Forward
| 2 | Reverse
MCC | 0 | Unspecified
| 1 | On | Start motor.
| 2 | Off | Stop motor.
SYSRC | 0 | Unspecified | Control mode unspecified
| 1 | Local | Local control mode
| 2 | Remote | Remote control mode
SYSRCS | 0 | Unspecified | Remote source is unspecified
| 1 | Remote Source 1 | Remote source 1
| 2 | Remote Source 2 | Remote source 2
SYS | 0 | Unspecified
| 1 | Booting | The system is booting up.
| 2 | Unconfigured | The system is waiting to be configured. This is the default system state after a factory reset.
| 3 | Ready To Run | The system has gone through the configuration process and is ready to run.
| 4 | Running Auto tuning | The system is auto tuning.
| 5 | Running Normal | The system is running normally and driving a motor.
| 6 | Running Emergency | The system is running in emergency mode. Most alarms are ignored.
| 7 | Running Maintenance | The system is in maintenance mode.
| 8 | Lockout | The system is in lockout and requires a power cycle to be reset.
| 9 | Shutting Down | The system is shutting down.
| 10 | Factory Reset | The system is applying a factory reset and will shut down after it is done.
| 11 | Fault | The system is in fault but can recover if the active fault(s) get resolved.
| 12 | Needs Autotuning | The system is configured but requires autotuning before being ready to run
| 13 | Running Degraded | System is running, with active alarms
| 14 | Hardware Test | System launched manufactoring scripts and is not in a clean state
| 15 | Software version change | System software is undergoing change
SYSR | 0 | No operation
| != 0 | Reset faults | Perform reset lockout.
MMODE | 0 | No operation
| 1 | Enabled | Activate Maintenance Mode
| 2 | Disabled | Deactivate Maintenance Mode
MBPID | 0 | SmartD
TBD
MCM | 0 | Unspecified | No mode has been set
| 1 | Frequency Mode | Drive is using frequency setpoint
| 2 | Preset frequency Mode | Drive is using preset frequency index setpoints
| 3 | Velocity Mode | Drive is using velocity setpoint
| 4 | Preset Velocity Mode | Drive is using preset velocity setpoint
| 5 | Torque Mode | Drive is using torque setpoint
N/A | 6 | Preset Torque Mode | Drive is using preset torque setpoint
PFOT | 0 | Unspecified | No type has been set
| 1 | Value | PID using forced output value
| 2 | Preset | PID using forced output preset
PIDOM | 0 | Unspecified | No mode has been set
| 1 | Control Mode | PID is in closed loop control mode (regulating)
| 2 | Forced Output Mode | PID is in Forced Output Mode
PIDPS | 0 | Unspecified | State is still unknown
| 1 | Disabled | PID instance is not enabled in [PIDConfiguration](#pidconfiguration).
| 2 | Off | PID instance is OFF
| 3 | Direct on | PID instance is in direct ON mode.
| 4 | Reverse on | PID instance is in reverse ON mode.
| 5 | Sleep | PID is in sleep mode
| 6 | Reserved
| 7 | Reserved
| 8 | Forced Output | PID forced output is enabled
| 9 | Motor disabled | Motor is disabled while PID is enabled
| 10 | Deadband | PID is in deadband state, holding constant until the setpoint has exited the deadband
| 11 | Constant output | PID is keeping the output constant
| 12 | Stopping | Stop was requested, PID is stopped and motor is currently stopping
AIMOD | 0 | Unspecified | No mode has been set
| 1 | Current | Analog input is configured for current
| 2 | Voltage | Analog input is configured for voltage
| 3 | Resistance | Analog input is configured for resistance
| 4 | PTC | Analog input is configured for PTC
Legend
Implemented
N/A | Not implemented

## Registers
Register |  | Bit is written in big-endian
AL1 | Alarm flags: |  | Read: 1 = alarm active, 0 = alarm inactive. Write: 1 = ack alarm, 0 = no operation.
|  | Bit 0 | Unspecified
|  | Bit 1 | STO
|  | Bit 2 | STO Loss
|  | Bit 3 | Line phase inversion
|  | Bit 4 | DC Undervoltage
|  | Bit 5 | DC Overvoltage
|  | Bit 6 | Line voltage sag
|  | Bit 7 | Line voltage balance
|  | Bit 8 | Line phase loss
|  | Bit 9 | HMI Communication Loss
|  | Bit 10 | Line current balance
|  | Bit 11 | Line overcurrent
|  | Bit 12 | Motor current balance
|  | Bit 13 | Motor overcurrent
|  | Bit 14 | Motor overtemp
|  | Bit 15 | Motor Overload
AL2 | Alarm flags: |  | Read: 1 = alarm active, 0 = alarm inactive. Write: 1 = ack alarm, 0 = no operation.
|  | Bit 0 | Drive overtemp
|  | Bit 1 | Unknown boot state
|  | Bit 2 | Booted backup software
|  | Bit 3 | Booted backup software with default config
|  | Bit 4 | Drive high temperature
|  | Bit 5 | Line voltage swell
|  | Bit 6 | Software update failed
|  | Bit 7 | DC single phased
|  | Bit 8 | Cooling fan 1 fault
|  | Bit 9 | Cooling fan 2 fault
|  | Bit 10 | Cooling fan 3 fault
|  | Bit 11 | Cooling fan 4 fault
|  | Bit 12 | Cooling Fan Capacity Fault
|  | Bit 13 | Line unexpected voltage
|  | Bit 14 | Low level comm errors
|  | Bit 15 | DC unbalanced
AL3 | Alarm flags: |  | Read: 1 = alarm active, 0 = alarm inactive. Write: 1 = ack alarm, 0 = no operation.
|  | Bit 0 | Drive output overcurrent
|  | Bit 1 | Simultaneous forward and reverse command
|  | Bit 2 | System boot time exceeded
|  | Bit 3 | System degraded
|  | Bit 4 | Abnormal CPU usage
|  | Bit 5 | Abnormal memory usage
|  | Bit 6 | DC Overvoltage stall prevention
|  | Bit 7 | Motor overcurrent stall prevention
|  | Bit 8 | Line unexpected frequency
|  | Bit 9 | DC Unexpected Frequency
|  | Bit 10 | AFE Fault
|  | Bit 11 | AFE Low voltage ride through
|  | Bit 12 | Remote to local override
|  | Bit 13 | Analog output sensor loss
|  | Bit 14 | PID 1 low process value
C |  | Bit 15 | PID 1 high process value
AL4 | Alarm flags: |  | Read: 1 = alarm active, 0 = alarm inactive. Write: 1 = ack alarm, 0 = no operation.
|  | Bit 0 | Control board power loss
|  | Bit 1 | Motor control instability
|  | Bit 2 | Motor overspeed
|  | Bit 3 | Motor Underspeed
|  | Bit 4 | Motor wrong direction
|  | Bit 5 | Encoder speed error
|  | Bit 6 | Encoder communication failure
|  | Bit 7 | Analog input 1 sensor loss
|  | Bit 8 | Analog input 2 sensor loss
|  | Bit 9 | Analog input 3 sensor loss
|  | Bit 10 | Modbus communication loss
|  | Bit 11 | High Ambient Temperature
|  | Bit 12 | Motor Temperature Sensor Shorted
|  | Bit 13 | Motor phase loss
|  | Bit 14 | Motor stalled
|  | Bit 15 | Motor disconnected
AL5 | Alarm flags: |  | Read: 1 = alarm active, 0 = alarm inactive. Write: 1 = ack alarm, 0 = no operation.
|  | Bit 0 | Motor application underload
|  | Bit 1 | Motor auto-restart failure
|  | Bit 2 | AFE low-voltage ride-through cannot recover
|  | Bit 3 | Drive overload
|  | Bit 4 | Invalid PIN code
|  | Bit 5 | Damper feedback loss
|  | Bit 6 | External start feedback timeout
|  | Bit 7 | External post stop feedback timeout
|  | Bit 8 | Motor ground fault
|  | Bit 9 | Emergency mode forbidden
|  | Bit 10 | External 1
|  | Bit 11 | External 2
|  | Bit 12 | External 3
|  | Bit 13 | External 4
|  | Bit 14 | Motor thermal overload
|  | Bit 15 | Internal MCU comm loss
AL6 | Alarm flags: |  | Read: 1 = alarm active, 0 = alarm inactive. Write: 1 = ack alarm, 0 = no operation.
|  | Bit 0 | BACNet comm loss
Bit 1
Bit 2
Bit 3
Bit 4
Bit 5
Bit 6
Bit 7
Bit 8
Bit 9
Bit 10
Bit 11
Bit 12
Bit 13
Bit 14
Bit 15
MBPV | MODBUS Profile version:
|  | Bit 0-7 | Minor version
|  | Bit 8-15 | Major version
DIS | Digital Inputs states: |  | Read: 1 = output is high, 0 = output is low, not configured, or configured for encoder
|  | Bit 0 | DI1 - Digital input 1
|  | Bit 1 | DI2 - Digital input 2
|  | Bit 2 | DI3 - Digital input 3
|  | Bit 3 | DI3 - Digital input 4
|  | Bit 4 | DI3 - Digital input 5
|  | Bit 5 | DI5 - Digital input 6
|  | Bit 6 to 15 | Reserved.
RELAYS | Relays states: |  | Read: 1 = energized, 0 = not energized
|  | Bit 0 | Relay 1
|  | Bit 1 | Relay 2
|  | Bit 2 | Relay 3
|  | Bit 3 to 15 | Reserved.